## To Do List
Specification Section 16050
WRC Systems Control - Electrical Checkout Procedure Checklist
Site Name:
Date:
Check-out Procedures. | In general, check-out procedures (as listed below) which are applicable for a particular item of equipment shall be performed:
ITEM COMPLETED BY CONTRACTOR (Y/N) | ITEM | NOTES
Vacuum interior of cubicles and remove foreign material.
Wipe clean with a lint-free cloth insulator, bushings, bus supports, etc.
Check and adjust time delay, under-voltage devices, phase relay, over-current relays, etc., as required by coordination study or ENGINEER.
Fill motor bearings requiring oil.
Check and change, as required, thermal overload heater elements to correspond with motor full-load current and service factors of installed motor.
Check direction of rotation of motors and reverse connections if necessary. Check rotation with motor mechanically uncoupled where reverse rotation could damage equipment.
Equipment with two or more sources of power connected by tie breakers, transfer switches, or generator receptacles shall be checked for rotation from each possible combination of power sources. Power sources must have the same phase sequence for each source throughout entire facility.
Check exposed bolted power connections for tightness.
Check operation of breakers, contactors, etc., and control and safety interlocks.
Check tightness of bolted structural connections.
Check leveling and alignment of enclosures.
Check operating parts and linkages for lubrication, freedom from binding, vibration, etc.
Check tightness and correctness of control connections at terminal blocks, relays, meters, switches, etc.
Clean auxiliary contacts and exposed relay contacts after vacuuming.